3GPP TSG-SA WG1 Meeting #92e	S1-204418

Online, 11 Nov – 20 Nov 2020                                          revision of S1-204098

Title:	Update to distributed automation use case

Agenda Item:	7.9.1

Source:	CEPRI, ZTE, China Telecom

Contact:	chenjie@epri.sgcc.com.cn

jiangshuai@epri.sgcc.com.cn

xu.ling@zte.com.cn

Abstract: This contribution proposes to rename the 5.3 to Feeder Automation and refine description according to Grid industry’s condition, then propose potential requirement.

Proposed Text:

5.3	 Use case of Distributed Feeder Automation

5.3.1	Description

With the increased requirements for more reliable, uninterrupted and continuous power supply, shorten the accident isolation time to milliseconds is required to support regional non-stop power services which make severe challenges for the master station in centralized distribution automation.

Therefore, intelligent distributed feeder automation has become one of the trends in the development of the power distribution grid. Its characteristics lie in the distributed sinking of the processing logic of the original master station to the intelligent power distribution terminal. Through the 5G communication among the intelligent power distribution terminals, intelligent judgment, analysis, fault location, fault isolation and non-fault area power supply restoration operations can be realized.

In this way, the fault handling process can be fully automated, the fault scope can be restricted and fault handling time of the distribution network can be decreased from seconds to milliseconds.

As illustrated in the Figure 5.3.1-1, the distributed feeder automation system is mainly composed of distribution master station, distributed monitoring terminal and the communication system. The distribution master station is mainly used for information gathering and human-computer interaction, and the distributed terminal is used for feeder status information collection, judgment, fault location, isolation and power supply restoration. The implementation result will be reported to the distribution master station. The  communication system is to provide the communication link among the distribution terminals.

The distribution master station is usually connected with the 5G system via wired or LAN which is out of 3GPP scope. Distribution master station manages multiple distributed terminals.

Each distributed terminal here is served by 5G UE to exchange its collected data with other distributed terminals. And from application aspect, the communication between distributed terminals is peer-to-peer. The connection between the distributed terminal and the 5G UE is out of 3GPP scope.

The 5G communication required here needs high reliability. Therefore at least two communication links are usually deployed for hot standby or transmitting data synchronously between two distributed terminals. Besides, once the communication link can’t support required communication service for distributed terminals, distributed terminal will block related functions automatically, in case of unexpected circuit breaker operation.

Figure 5.3.1-1 Example of distributed feeder automation architecture

GOOSE protocol is a burst based transmission application protocol used in smart grid. During the feeder system normal working phase, the heartbeat packet is periodic transmitted with 1s. When a fault occurs, it performs incremental periodic transmission from 2ms, 8ms, 16ms to 32ms. After there is no sudden change in collected data, the heartbeat packet transmission of 1s is restored.

5.3.2	Pre-Conditions

Chinese Distributed Grid can be divided into urban and agricultural parts. In urban area, the power load is relatively concentrated, and the distributed grid working environment is better. But in the agricultural area, the power service range is very large, while the distributed grid has to face so many issues e.g. a large number of harmonic sources, three-phase unbalance, voltage flicker pollution.

Two 5G communication links are deployed for hot standby or transmitting data synchronously between UEs in distributed terminals and the network.

5.3.3	Service Flows

1.Data collection: The distributed terminal collects and reports related status information to the distribution master station or other distributed terminals in real time.

2.Fault detection and localization: The distributed terminal collects fault signal from itself and neighboring terminals. Then it executes data processing and fault location logic and judges the fault whether an instantaneous or permanent fault.

2a. When the distribution fault is an instantaneous fault, the feeder automation process will not be triggered.

2b. When the fault is a permanent fault, the distributed terminal will locate the feeder fault based on the signals of each power distribution terminal. The upstream power distribution terminal of the node will continue to send status information, while the downstream power distribution terminal will not report the fault signal. Therefore, in the corresponding fault node, only one switch should send out the fault signal. According to this feature, when a feeder fault occurs, every distributed terminal could judge its position relative to the fault location.

3.Fault isolation: When the fault node is determined, according to the preconfigured action order, all switches around the faulty node will open to realize effective identification and isolation of the faulty area.

4.Fault restoration: For the restoration of power supply in non-fault area, it is necessary to clarify the number and wiring of the switches it tied to, e.g. when a fault occurs in the cabinet of the one-in-two-out ring main unit, if two outgoing lines have isolated power-loss area, the related distributed terminals will reconstruct the power distribution structure, and close the tie switch, to restore the power supply in the power-loss area.

5. Restoration confirmation: After the power supply is restored in the power-loss area, the system needs the distribution terminals report status information to determine whether the restoration is well done.

5.3.4	Post-Conditions

It can identify and shorten the power feed accident isolation time to milliseconds and support regional non-stop power services.

5.3.5	Existing features partly or fully covering the use case functionality

The 5G system shall be able to provide connection service wherever the power terminal is indoor, outdoor, low and medium altitude, or underground.

Editor note: It is FFS whether and how to address providing connection service to underground access for distributed automation grid applications.

The 5G system shall be able to provide suitable APIs to enable application layer to monitor communication link status.

5.3.6	Potential New Requirements needed to support the use case

[PR 5.3.6 - 1]The 5G system shall be able to provide at least two back up communication links between every UE in a distributed terminal and the network.

[PR 5.3.6 - 2]The 5G system shall be able to provide required communication service according to KPI given in table 5.3.6-1 (NOTE 1)

Table 5.3.6-1 KPI for Distributed Feeder Automation

| User experienced Data rate (bps) |  | Latency (ms) (note2) |  | Latency jitter (us) (note3) |  | Synchronicity budget requirement (us) |  | Reliability % |  | Connection density |  | coverage |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2-10M | <10 | <50 |  | <10 | 99.999 | [x]*10/km2 | <40km (city range) |
| NOTE 1: refer [3] NOTE 2: refer [3], the data transmission time from one distributed terminal to the peer distributed terminal should be less than 20ms. So, the one way latency is less than 10ms. NOTE 3: the latency jitter is required for the switch off between the active and standby communication links while the communication links distance <40km. Editor’s Note: the "x" in the table with real value will FFS. |  |  |  |  |  |  |  |  |