3GPP TSG-SA WG1 Meeting #91e	S1-203084

Electronic Meeting, 24-31 August 2020	(revision of S1-203xxx)

Title:	Use case on timing and timing resiliency delivery to smart grid

Agenda Item:	7.8.1

Source:	Nokia, Nokia Shanghai Bell

Contact:	Betsy Covell	betsy.covell@nokia.com

Abstract: This contribution proposes a use case for timing and timing resiliency delivery to smart grid. This contribution has been prepared in collaboration with ABB Group’s Design Architect, Petri Syväluoma and Research Program Manager Petri Hovila.

Proposed New Text:

***** Text below is all new, shown without change marks for readability ******

## 5.x	Use Case on 5GS timing resiliency for smart grids

### 5.x.1	Description

The focus for this use-case description is power sub-stations where robust time synchronization is needed for e.g., synchro phasor and other Smart Grid applications.

### 5.x.2	Pre-conditions

Power sub-systems use wireless means to achieve time synchronization, as is the case today leveraging GNSS receiver capabilities. In today’s power sub-system the timing resiliency is based on e.g., having multiple grandmasters leveraging multiple GNSS receivers. In this use case 5GS is used as a supplement to, e.g., integrated as alternative radio in the grandmaster clock or as an alternative grandmaster clock with 5G capability in the power sub-system, or alternative to the GNSS, e.g., integrated with PTP grandmaster clock avoiding installation of external GNSS antenna and receiver at the power sub-station.

In this use case, the smart grid is subscribed to and authorized to use the 5G timing resiliency service to ensure reliable timing signals are always available.  The 5G timing resiliency service monitors the accuracy and availability of timing signals from a designated timing source and is able to provide an alternate source (e.g., 5G holdover capacity, atomic clock) in case of failure in the primary source.  An SLA may be in place to establish the primary and any alternate timing sources that can be used.

### 5.x.3	Service flows

This section should also describe how the timing resiliency is enhanced when the 5GS is used in conjunction with the GNSS, how the system is notified of a failure of GNSS, how the 5GS picks up the slack to keep the system running smoothly in the absence of GNSS. The UEs are preconfigured to enable the provision of time synchronization service from the 5GS. In addition to the initial pre-configuration the UEs may have, additional information may be used for dynamically configuring the management of the 5GS time synchronization network within the smart grid system.

The configuration of the smart grid system includes timing service from GNSS with resiliency support provided by 5GS. Based on the 5G time resilience requirements, the time distribution method used, and type of time synchronization  device connected to the UE (e.g., DS-TT), the 5GS may configure different network entities (i.e., gNBs, UEs/DS-TTs, UPFs/NW-TTs) and the behaviour when an issue is detected (e.g., notification towards the UE or application, back-up configuration).

The 5GS detects that the GNSS is experiencing a problem (e.g., loss of satellite access, detection of inconsistent timing information, detection of drop in QoS).

The 5GS communicates the loss of GNSS to UEs or applications subscribed to the timing resilience service. Additionally, the 5GS may indicate the UEs should use the timing service provided by the 5GS until further notice instead of GNSS signal. The 5GS is configured to provide an accurate timing service for a specified holdover time. Depending on the detected problem and the impacted area, the 5GS may reconfigure its own network to ensure the distribution of an accurate timing service to the UEs.

The 5GS provides timing information to the UEs using a secure mechanism.

The UEs are able to verify the integrity and accuracy of the timing information provided by the 5GS.

The 5GS continues to monitor for a return to service by the GNSS. When the GNSS service recovery is detected, the 5GS informs the UEs or application subscribed to the resilience timing service that they can again receive GNSS timing information.

### 5.x.4	Post-conditions

The Smart Grid can use 5GS as a resiliency backup to their GNSS receiver based (or wired) time synchronization systems to improve availability and reliability of the time synchronization. Alternatively, existing GNSS receiver-based solutions may be replaced with a 5GS based solution where it improves efficiency and/or reliability.

### 5.x.5	Existing feature partly or fully covering use case functionality

Many 5GS features specified in Release-16 and expected in Release-17 will be required for the use-case:

- Time synchronization to UTC leveraging 5GS C-Plane and/or U-Plane

- Support for IEEE 1588 PTP

- Propagation delay compensation, to ensure that time synchronization can be conducted accurately across wide area deployments needed for power sub-station support

- Exposure framework supports time synchronization based on the needs of the service

### 5.x.6	Potential new requirements and KPIs

#### 5.x.6.1 Potential Requirements

[PR 5.x.6.1-1] The 5G system shall monitor for timing service failure (e.g., detect QoS degradation)

[PR 5.x.6.1-2] The 5G system shall be able to indicate to devices (e.g., UEs, application servers) using a timing service that they need to use an alternate source (e.g., use 5GS with internal holdover resiliency or an alternate source, e.g. atomic clock, Sync over Fiber, TBS).

[PR 5.x.6.1-3] The 5G system shall support a holdover capability (maintaining UTC required accuracy) of up to 24h.

[PR 5.x.6.1-4] A time synchronization device connected to the 5G system shall support a holdover capability of >5s.

[PR 5.x.6.1-5] The 5G system shall be able to detect and indicate to devices (e.g., UEs, application servers) when GNSS reference timing signals are restored for network time synchronization.

#### 5.x.6.2 Potential KPIs

Table 5.x.6.2-1: Timing resiliency service performance requirements for 5G System

| Use-case | Holdover Time | Sync Target | Sync accuracy | Service area | Mobility | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Power grid (5G network) | Up to 24 hour | UTC (note 1) | [<250ns] | < 20 km2 | low | When 5G System provides direct PTP Grandmaster capability to sub-stations |
| Power grid (time synchronization device) | >5 s | UTC (note 1) | [<250ns] | < 20 km2 | Low | When 5G sync modem is integrated into PTP grandmaster solution (with 24h holdover capability) at sub-stations) |
| Note 1: Different synchronization target is acceptable as long as offset is preconfigured if 5G provide time differs from GNSS. In this case, 5G end device shall provide PPS output which can be used for measuring the difference. |  |  |  |  |  |  |