3GPP TSG-SA WG1 Meeting #91e	S1-203082

Electronic Meeting, 24-31 August 2020	(revision of S1-203xxx)

Title:	FS_5TRS Overview

Agenda Item:	7.8.1

Source:	Nokia, Nokia Shanghai Bell

Contact:	Betsy Covell	betsy.covell@nokia.com

Abstract: This contribution proposes text for the Overview clause in TR 22.878.  This text describes how a 5G timing resiliency service can be used in the smart grid sector. This contribution has been prepared in collaboration with ABB Group’s Design Architect Petri Syväluoma and Research Program Manager Petri Hovila.

Proposed Text Changes:

# 2	References

The following documents contain provisions which, through reference in this text, constitute provisions of the present document.

-	References are either specific (identified by date of publication, edition number, version number, etc.) or non-specific.

-	For a specific reference, subsequent revisions do not apply.

-	For a non-specific reference, the latest version applies. In the case of a reference to a 3GPP document (including a GSM document), a non-specific reference implicitly refers to the latest version of that document in the same Release as the present document.

## 2.1 Normative references

[1]	3GPP TR 21.905: "Vocabulary for 3GPP Specifications".

[X1]	National Institute of Standards and Technology (NIST), “Timing Challenges in the Smart Grid”, accessed at https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.1500-08.pdf, January 2017

[X2 ]	61850-9-3-2016 - IEC/IEEE International Standard - Communication networks and systems for power utility automation – Part 9-3: Precision time protocol profile for power utility automation, https://standards.ieee.org/standard/61850-9-3-2016.html#Standard

[X3]	IEEE 1588-2008, IEEE Standard for a Precision Clock Synchronization Protocol for Networked Measurement and Control Systems.

## 2.2 Informative References

[X4] 	Used with permission from ABB Distribution Solutions.

## 3.2        Abbreviations

For the purposes of the present document, the abbreviations given in 3GPP TR 21.905 [1] and the following apply. An abbreviation defined in the present document takes precedence over the definition of the same abbreviation, if any, in 3GPP TR 21.905 [1].

SCADA	Supervisory control and data acquisition

SNTP	Simple Network Time Protocol

***** Text below is all new, shown without change marks for readability ******

# 4	Overview

## 4.1 Applicability of 5G timing resiliency service in the smart grid sector

### 4.1.1 General

Power grids are critical to the world economy as most other critical infrastructure including communications depend on them. Electric utilities are transitioning towards smart power grids to enhance efficiency and reliability, with real-time measurements and control between smart devices in the field with centralized data facilities running intelligent analytics.

The timing solutions for Smart Grid must address a significant list of concerns. Time synchronization is in general considered a key security vulnerability of Smart Grids, and an area of direct relevance to timing resiliency systems and the 5G System is ensuring timing integrity, e.g., providing solutions to the increasing prevalence of satellite signal loss, jamming, and the potential for spoofing [X1]. Power utility companies do not want to be dependent only on satellite-based time synchronization due to several factors:

- Interference: Either caused intentionally or by environment (e.g. solar flares).

- Governmental decision: Public time synchronization service can be disabled or weakened remotely; GPS selective availability as an example.

- Maintenance: Changing the faulty GPS antenna may take some time.

- Other: Long downtime time when updating or fixing satellite systems; Galileo downtime of 100h as an example. As a comparison, 24h holdover time has been specified for power systems.

Although there are a large range of applications possible in Smart Grids in need of timing resiliency, the focus here is mainly on power sub-stations where robust time synchronization is needed for e.g., synchro phasor applications. Those are relevant for 5G System-based timing resiliency solutions and simultaneously represent the most demanding application in terms of required time synchronization performance. However, other applications are also mentioned and captured.

### 4.1.2	Timing Accuracy

Precise timing is key to operating the smart power grid. One area relates to controlling the frequency (50Hz/60Hz), while another area relates to providing events with timestamped measurement values, with required accuracies down to a few hundred nanoseconds [X1]. Correct timing is a key enabler for communication and orchestration of technologies for accurate and optimal wide area monitoring, protection and control in the power industry [X1].

In a typical smart grid architecture, centralized monitoring systems have visibility to events occurring in a distributed hierarchy of substations and distribution systems.  Having very accurate timing across the endpoints allows the monitoring systems to readily detect faults, identify the source and extent of impact, and take corrective action in a manner affecting the smallest possible portion of the grid. For such event reporting, a 1ms timing accuracy is sufficient.

Figure 4.1.2-1: Time stamped events [X4]

Timing accuracy is also needed for power system measurements for fault detection in the current phase. Recordings of the phase may be triggered at various points when a fault is detected.  Running analysis on multiple time-aligned recordings can provide a clear picture of the extent of impact. For reliable analysis, 1 ms timing accuracy is typically needed across all recordings and is today limited mostly by SNTP time sync methods typically in use.

Figure 4.1.2-2: Current disturbance recoding [X4]

Monitoring the power system frequency also requires timing accuracy for fault detection and resolution. In this case, accuracy between 1 µs to 10 µs is needed to provide accurate correlation of frequency.

Figure 4.1.2-3: Frequency synchronization [X4]

Finally, the accuracy needed depends on the timing role of the component within the power sub-system. E.g. a PTP slave within the sub-network generally needs to fulfil the application requirements as discussed above (e.g. down to 1s accuracy requirement) whereas a component that is a PTP Grand Master needs to be accurate to a 250 ns requirement[X2]

4.1.3 Timing Resiliency

A simple overview of a power sub-station is provided in Figure 4.1.3-1. In a typical deployment today, the sub-station achieves time synchronization by means of a grandmaster clock that uses the IEEE 1588 Precision Time Protocol (PTP) [X3] protocol to synchronize elements inside the power sub-station via an Ethernet connection. The grandmaster clock often uses a GNSS receiver to achieve time synchronization information. To access the GNSS signal, an external GNSS antenna is typically required. The figure shows how time and communication redundancy can be achieved within substation by means defined in IEC 62439-3:2016 [X2]. However, since the time source (GNSS) illustrated is a single point of failure (e.g. whenever satellite(s) are not available or there is interference), 5G is a candidate resiliency solution.

Figure 4.1.3-1: Example power sub-system setup leveraging 2x GNSS based clock grandmasters [X4]

The GNSS receiver elements of the clock grandmaster installed in power-subsystems have some desirable characteristics including intrinsic multi-layer jamming and spoofing detection capabilities, e.g., autonomous disruption detection and intelligent protection and control. The timing accuracy requirement of the GNSS receiver is <250 ns according to the grandmaster requirements listed in [X3]. This allows sufficient budget for synchronization distribution errors within the power sub-station versus the E2E requirements of the Smart Grid operation (e.g., where every PTP slave needs to be synchronized to a <1 s accuracy).

Many power sub-systems already have cellular 4G coverage. A 5G System-based timing solution offers multiple potential enhancements, including:

- As a resiliency solution to the GNSS received timing solution if GNSS fails or is compromised, e.g., integrated as alternative radio in each grandmaster clock or as an alternative grandmaster clock with 5G capability in the power sub-system.

- As an alternative to GNSS use, e.g., integrated with PTP grandmaster clock avoiding installation of external GNSS antenna and receiver at the power sub-station.

These alternatives are illustrated in Figure 4.1.3-2. In both cases, time synchronization may be provided from the 5G System to 5G sync modem by either C-Plane method (e.g. via System Information Broadcast or unicast RRC messaging) or using PTP method according to the power sub-system configuration requirements.

The latter requires also some actions from the 5G System in case time source is lost is missing, e.g., similar to IEC 61850-9-3, clockClass should be dropped when the 5G System is in holdover state. Further, PPS output has significant use-cases and is commonly used today and can be desired property of 5G sync modem.

Figure 4.1.3-2: 5G integration into system – resilience and alternative mode

Another key requirement is holdover capability, the ability to continue providing accurate timing service in the event of loss of an external source (e.g., GNSS), for the 5G System. For option (a) in Figure 4.1.3-2 a 24h holdover capability is automatically supported as this is the case for today’s distributed solution where GM1 and GNSS is always one and the same device. 5G modem functionality could be either integrated into the same device as a chip or as an input using option (b) type external modem, e.g., for this case, no specific holdover capability is required from the 5G System. With option (b), holdover capability is mainly determined by the 5G network. Here it is desirable that the 5G sync modem has a holdover capability of at least 5s to comply with [X2] and that the 5G network can support up to 24h of holdover capability. However, as option (a) can be a solution when 24h holdover capability is strictly needed for the power utility, this requirement could be more scalable, e.g. allow for wider range of performance of 5G networks and 5G sync modems with exploiting also hold-over capability (stability) of GM1.

High level requirements to the 5G System to support these alternatives are highlighted in Table 4.1.3-1

Table 4.1.3-1 High level requirements for 5G timing resiliency in smart grid

| Area | Requirement |
| --- | --- |
| Time Domain | UTC, delivered from network to end-point device in power sub-station. An absolute time difference to GPS/GNSS is acceptable (can be preconfigured) as long as 5G end device provides PPS output which can be used for measuring the difference. |
| Deployment | Wide area support is needed to reach power sub-systems, e.g., should support full coverage requirements. Mobility is low, e.g., power sub-systems are static structures. Public Network: - Minimum density 5 devices per km2 - Maximum density 100 devices per km2 Private Network: - Up to 1000 devices per km2 |
| Mobility | None, synchronization devices are static and vehicles connect to grid in a static location when in need of time synchronization. |
| Synchronization accuracy (examples) | <250-1000 ns for synchro phasor use-cases, e.g., to supplement/replace existing GNSS receiver based solutions 1:1. <1-10 s for Power system protection and synchronization <1 ms for Event reporting use-cases, Disturbance recording use-cases |
| Holdover capability | Up to 24h for 5G network, e.g. the 5G network needs to maintain its ability to synchronize power sub-systems even after general loss or failure of UTC time source. >5s for 5G sync modem [X2] |
| Timing delivery method | Provided from 5G System to 5G sync modem either via SIB9/unicast signalling or IEEE PTP messaging. When the 5G System provides PTP to the power sub-station network (e.g. 5G System directly supplies PTP messages for a 5G time domain) the selection of the time source should be based on clockClass and clockAccuracy. IEC 61850-9-3 7.4.3 [X2] defines clockClass behaviour for Power utility profile. PPS capability of a 5G sync modem is desirable for many use-cases. A device with the capability for both GNSS and 5G timing will monitor internal signals or external PTP and internal GNSS signal depending on the configuration. |
| Services provided by 5G System | Time resilience service provides 5G clock properties, e.g., clockClass, accuracy, etc to reflect the possible selection of clock source e.g., during GNSS unavailability. When acting as a backup or replacement time source, the 5G System provides secure timing service to UEs and application servers. |